Temperature Transmitter Communication Protocol

V2.1

I. Overview

This communication protocol adopts standard Modbus protocol, and the transmission mode used is RTU mode. Modbus protocol is a master-slave protocol.

Only one device can transmit on the wire at any one time. The exchange of information is managed by the master and only it can initiate. It polls the slaves successively. No slave can send a message unless approved by the master. Direct communication between slave stations is not possible.

The protocol frame does not contain any message header bytes or message byte terminators.

It is defined as follows:

| Slave address | Request code | Data | CRC16 |
| --- | --- | --- | --- |

Slave Address:- The address must be between 1 and 247.

- Each address must be unique within the context of the network device.

Data: transmitted in binary code.

CRC16: Cyclic Redundancy Check parameter.

When the interval is longer than or equal to 3.5 characters, the end of frame is detected.

1.Communication port settings

Communication method Asynchronous serial communication interface, such as RS-485, RS-232, RS-422, etc.

Baud rate 1200, 2400, 4800, 9600, 14400, 19200bps (can be changed by setting instrument parameters, default 9600)

2. Byte data format

.one start bit

.Eight data bits

.Even parity

.One stop bit

| Start | D0 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | even parity | Stop |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

2. Instrument communication frame format

(1) Definition of terms

● Slave number:

The local instrument address, the address must be between 1 and 255, and the address of each instrument on the same bus cannot be repeated. When the address is 0, it is used for the broadcast function, and only the write function is valid at this time, and the slave station does not respond. single byte.

● Function code:

The "read" and "write" functions are defined from the master point of view. single byte.

| Function code | Modbus name | Function name | Broadcast | The maximum value of N in a row |
| --- | --- | --- | --- | --- |
| 3 (0x03) | Read Holding Registers | Read N register values | NO | 9 |
| 16 (0x10) | Write Multiple Registers | Write N register values | YES | 9 |

● First register address:

Address of the first internal register to read. Double byte, high byte first.

● Number of registers:

The number of internal registers to be read or modified consecutively. Double byte, high byte first.

● Number of bytes:

The total number of bytes of data for all registers that were read or written. single byte.

● CRC16:

Cyclic redundancy check parameters. Double byte, low byte first.

(2) Read and write operations

1) Read N output words: function code 3 (0x03)

Note: Hi = high byte, Lo = low byte.

This function can be used to read parameters regardless of type.

master request

| Slave number | 0x03 | first register address |  | Number of registers |  | CRC16 |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Hi | Lo | Hi | Lo | Lo | Hi |

1 Byte          1 Byte             2 Byte                  2 Byte                 2 Byte

Slave response

| Slave number | 0x03 | bytes read | first register value |  | …… | last register value |  | CRC16 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Hi | Lo |  | Hi | Lo | Lo | Hi |

1 Byte      1 Byte       1 Byte         2 Byte                      2 Byte           2 Byte

Example 1: Using function 3 to read 1 unit on slave 1 (address 0003H)

master request

| 0x01 | 0x03 | 0x00 | 0x03 | 0x00 | 0x01 | 0x74 | 0x0A |
| --- | --- | --- | --- | --- | --- | --- | --- |

1 byte        1 byte             2 byte                  2 byte                  2 byte

Slave response

| 0x01 | 0x03 | 0x02 | 0x00 | 0x11 | 0x78 | 0x48 |
| --- | --- | --- | --- | --- | --- | --- |

1byte          1byte         1 byte                2 byte                    2 byte

2) Write N output words: function code 16 (0x10)

master request

| Slave number | 0x10 | first register value |  | Number of registers |  | number of bytes | first word data |  | …… | CRC16 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Hi | Lo | Hi | Lo |  | Hi | Lo |  | Lo | Hi |

1 byte   1 byte        2 byte             2 byte           1 byte          2 byte                   2 byte

Slave response

| Slave number | 0x10 | first register address |  | Number of registers |  | CRC16 |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Hi | Lo | Hi | Lo | Lo | Hi |

1 byte     1 byte             2 Byte                         2 Byte                        2 Byte

Example 2: Write 1000, 200 to 2 units in slave 1 using function 16 (register addresses 0009H to 000AH)

master request

| Slave number | request code | first register address |  | Number of registers |  | number of bytes | first register data |  | second register data |  | CRC16 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0x01 | 0x10 | 0x00 | 0x09 | 0x00 | 0x02 | 0x04 | 0x03 | 0xE8 | 0x00 | 0xC8 | 0xB2 | 0x23 |

Slave response

| Slave number | response code | first register address |  | Number of registers |  | CRC16 |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 0x01 | 0x10 | 0x00 | 0x09 | 0x00 | 0x02 | 0x91 | 0xCA |

3) Abnormal response

When the slave cannot execute the request sent to it, it will return an exception response.

Format of exception response:

| Slave number | response code | error code | CRC16 |  |
| --- | --- | --- | --- | --- |
|  |  |  | Lo | Hi |

1 byte     1 byte      1byte          2 byte

Response code: Requested function code + 0x80 (most significant bit is set to 1).

error code:

1 = Request to access a register address that is not within the register address range.

2 = The number of registers to be accessed at one time in the request exceeds the maximum number of registers that can be accessed consecutively.

3 = Slave write protection (see the baud rate menu settings in the manual for details).

3. The address table corresponding to the internal parameters of the TT-510 intelligent temperature meter head (range: 0x0000-0x0018):

| Numbering | parameter notation | parameter name | register address (hex) | Data Format (hex) | Attributes | Value range (decimal) | Remark |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | PV | Process value | 0000 | double byte signed | Read | -32768~32767 | Unit 0.1℃ |
| 1 | Prty | Check method | 0001 | double byte unsigned | Read/Write | 0 - no checksum 1 - odd parity 2 - even parity | Note[1]: no decimal point |
| 2 | UAd | Meter address | 0002 |  | Read/Write | 1～255 |  |
| 3 | Ucr | Instrument communication baud rate | 0003 |  | Read/Write | 0～6 |  |
| 4 | Key | Calibration password | 0004 | double byte unsigned | Read/Write | 0xA5A5 is valid | Note[10]: The password can only be calibrated after passing |